NUMERO MASSIMO DI SCHEDINE PRAESIDEO REL.2.2
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Up to 80 end

-

of

-

line and loudspeaker supervision boards can be 

addressed by each Praesideo power amplifier

–

80 boards on a 500W amplifier channel (80 on a LBB4421)

–

40 boards on a 250W amplifier channel (80 on a LBB4422)

–

20 boards on a 125W amplifier channel (80 on a LBB4424)

–

(10 boards on a 60W amplifier channel (80 on a LBB4428))

•

Per channel not more than 16 end

-

of

-

line supervision boards

•

BUT

upgraded LBB442x

/10

amplifiers are required

–

LBB4421/10, LBB4422/10, LBB4424/10 available with V2.20

–

LBB4426/00 will go end

-

of

-

life, no upgrade, compensated by

price decrease of LBB4424 and LBB4428

–

LBB4428/10 expected with V2.40 (Dec 2005)


OVVERO

· LBB4421/10 : AMP PRAESIDEO 1*500W fino a 80 schedine (fine linea + schedine altoparlante) 

· 1 schedina main LBB4440/00 

· da 0 a max 16 EOL LBB4443/00

· nr. max LSP Board LBB4441/00 consentito: differenza 80 – nr. totale schedine EOL 

· LBB4422/10 : AMP PRAESIDEO 2*250W fino a 80 schedine (fine linea + schedine altoparlante) 

· 2 schedine main LBB4440/00 

· max 16 EOL x canale = max 32 schedine fine linea LBB4443/00

· nr. max LSP Board LBB4441/00 consentito: differenza 80 – nr. totale schedine EOL

· LBB4424/10 : AMP PRAESIDEO 4*125W fino a max 80 schedine (fine linea + schedine altoparlante) 

· 4 schedine main LBB4440/00

· max 16 EOL x canale = max 64 schedine di fine linea LBB4443/00

· nr. max LSP Board LBB4441/00 consentito: differenza 80 – nr. schedine EOL

NOTE: 

LBB4441/00 E’ possibile installare solamente le schedine altoparlante senza EOL 

LBB4442/00 E’ possibile continuare ad utilizzare le schedine con nuova rel 2.20 solo sulle linee principali altoparlante

The MTTR of Praesideo depends on how the service is locally organized.

We can reach a MTTR of 30 minutes when spare commercial type numbers are used at the system.

The maximum time of 3 to 4 weeks MTTR can be reached when no local arrangements are made and the defective unit will be send for central repair.

Common is to use a MTTR suitable for the customers. This could means that or the installer should calculated in extra unit (spare amplifiers for example) Or that the NSO arranges a local solution with the service partner: local swap/repair stock. Because we will extend the spare parts to modules and PCB's in the near future (what we have now is the Input board and power supply modules as sspare parts) less stock of complete type numbers is needed. 

A common time to replace the power supply module or the input PCB is 1 hour.

Please see also the Service Marketing plan for official MTTR information
