DS-1LN5EPSL3

F/UTP Cat5E LSZH 24AWG CPR Cca Cable

Feature and Function

- Stable electrical performance, compliant with ANSI/TIA-568.2-D, IEC61156, ISO/IEC11801.

- Compliant with RoHS 2.0.

- Sheath with strong mechanical properties, and high tensile and compressive strength, reducing damage during the project.

- Excellent performance in the Fluke 90-meter permanent link test while working continuously at 50°C high temperature.

- Excellent performance in the Fluke 100-meter channel test while being continuously loaded with 57 V/1 A DC power (PoE).

- Solid-Bare Copper conductor with less resistance, and better electrical properties and transmission performance.

Specification

| Model | DS-1LN5EPSL3 |  |
| --- | --- | --- |
| Category | Cat.5E |  |
| Sheath printing | HIKVISION NETWORK CABLE CAT5E F/UTP 24AWG LSZH CPR Cca VERIFIED TO ANSI/TIA-568.2-D ****m mm/dd/yyyy xx |  |
| Reference standard | ISO/IEC11801, ANSI/TIA-568.2-D, RoHS 2.0 |  |
| Fire resistance | CPR Cca s1b d1 a1 |  |
| Conductor | Material | Solid-Bare Copper (99.95%) |
|  | Diameter | 0.50 ± 0.005 mm 24AWG |
| Insulation | Material | HDPE |
|  | Diameter | 0.98 ± 0.05 mm |
| Sheath | Thickness | 0.60 ± 0.10 mm |
|  | Diameter | 6.20 ± 0.40 mm |
|  | Material | LSZH |
|  | Color | Blue |
| Rip-cord | Yes |  |
| Separator | No |  |
| Sheath physical properties | Before aging | Tensile strength ≥ 9.0 Mpa Elongation ≥ 100% |
|  | Aging period | 100°C × 24h × 10d |
|  | After aging | Tensile strength ≥ 8.0 Mpa Elongation ≥ 70% |
|  | Cold bend | -20 ± 2°C × 4h, 8 × cable O.D, no visible cracks |
| Electrical Characteristics (20°C) | 1.0-100.0 MHz impedance | 100 ± 15 Ω |
|  | 1.0-100.0 MHz delay skew | ≤ 45 ns/100 m |
|  | DC resistance | ≤ 9.38 Ω/100 m |
|  | DC conductor resistance unbalance | ≤ 4.0% |
|  | Package dimension | 380 mm (W) × 380 mm (H) × 220 mm (D) (14.96" × 14.96" × 8.66") |
|  | Weight | 14 ± 1kg |
|  | Cable length | (305 ± 1.5) m |
|  | Ambient temperature | -20°C to 75°C (-4°F to 167°F) |
|  | Operating voltage | 57 V |

Technical Performance (100 m)

| Frequency (MHz) | ATT (20 ℃) ≤ (dB) | RL ≥(dB) | NEXT ≥(dB) | PS NEXT ≥(dB) | EL FEXT ≥(dB) | PS EL FEXT ≥(dB) | Phase delay ≤(ns) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2.0 | 20.0 | 65.3 | 62.3 | 63.8 | 60.8 | 570 |
| 4 | 4.1 | 23.0 | 56.3 | 53.3 | 51.8 | 48.8 | 552 |
| 8 | 5.8 | 24.5 | 51.8 | 48.8 | 45.7 | 42.7 | 547 |
| 10 | 6.5 | 25.0 | 50.3 | 47.3 | 43.8 | 40.8 | 545 |
| 16 | 8.2 | 25.0 | 47.2 | 44.4 | 39.7 | 36.7 | 543 |
| 20 | 9.3 | 25.0 | 45.8 | 42.8 | 37.8 | 34.8 | 542 |
| 25 | 10.4 | 24.3 | 44.3 | 41.3 | 35.8 | 32.8 | 541 |
| 31.25 | 11.7 | 23.6 | 42.9 | 39.9 | 33.9 | 30.9 | 540 |
| 62.5 | 17.0 | 21.5 | 38.4 | 35.4 | 27.9 | 24.9 | 539 |
| 100 | 22.0 | 20.1 | 35.3 | 32.3 | 23.8 | 20.8 | 538 |

Available Model

DS-1LN5EPSL3