DS-1LN6USL3

U/UTP Cat6 LSZH 23AWG CPR Cca Cable

Feature and Function

- Stable electrical performance, compliant with ANSI/TIA-568.2-D, IEC61156, ISO/IEC11801.

- Compliant with RoHS 2.0.

- Sheath with strong mechanical properties, and high tensile and compressive strength, reducing damage during the project.

- Excellent performance in the Fluke 90-meter permanent link test while working continuously at 50°C high temperature.

- Excellent performance in the Fluke 100-meter channel test while being continuously loaded with 57 V/1 A DC power (PoE).

- Solid-Bare Copper conductor with less resistance, and better electrical properties and transmission performance.

Specification

| Model | DS-1LN6USL3 |  |
| --- | --- | --- |
| Category | Cat.6 |  |
| Sheath printing | HIKVISION NETWORK CABLE CAT6 U/UTP 23AWG LSZH CPR Cca VERIFIED TO ANSI/TIA-568.2-D ****m mm/dd/yyyy xx |  |
| Reference standard | ISO/IEC11801, ANSI/TIA-568.2-D, RoHS 2.0 |  |
| Fire resistance | CPR Cca s1a d0 a1 |  |
| Conductor | Material | Solid-Bare Copper (99.95%) |
|  | Diameter | 0.565± 0.005 mm 23AWG |
| Insulation | Material | HDPE |
|  | Diameter | 0.98 ± 0.05 mm |
| Sheath | Thickness | 0.50 ± 0.05 mm |
|  | Diameter | 6.20 ± 0.50 mm |
|  | Material | LSZH |
|  | Color | Blue |
| Rip-cord | Yes |  |
| Separator | Yes |  |
| Sheath physical properties | Before aging | Tensile strength ≥ 10.0 Mpa Elongation ≥ 125% |
|  | Aging period | 100°C × 24h × 10d |
|  | After aging | Tensile strength ≥ 8.0 Mpa Elongation ≥ 100% |
|  | Cold bend | -20 ± 2°C × 4h, 8 × cable O.D, no visible cracks |
| Electrical Characteristics (20°C) | 1.0-250.0 MHz impedance | 100 ± 15 Ω |
|  | 1.0-250.0 MHz delay skew | ≤ 45 ns/100 m |
|  | DC resistance | ≤ 9.38 Ω/100 m |
|  | DC conductor resistance unbalance | ≤ 4.0% |
|  | Package dimension | 400 mm (W) × 400 mm (H) × 255 mm (D) (15.75" × 15.75" × 10.04") |
|  | Weight | 15 ± 1kg |
|  | Cable length | (305 ± 1.5) m |
|  | Ambient temperature | -20°C to 75°C (-4°F to 167°F) |
|  | Operating voltage | 57 V |

Technical Performance (100 m)

| Frequency (MHz) | ATT (20 ℃) ≤ (dB) | RL ≥(dB) | NEXT ≥(dB) | PS NEXT ≥(dB) | EL FEXT ≥(dB) | PS EL FEXT ≥(dB) | Phase delay ≤(ns) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2.03 | 20.0 | 74.3 | 72.3 | 67.8 | 64.8 | 570 |
| 4 | 3.78 | 23.0 | 65.3 | 63.3 | 55.8 | 52.8 | 552 |
| 8 | 5.32 | 24.5 | 60.8 | 58.8 | 49.7 | 46.7 | 547 |
| 10 | 5.95 | 25.0 | 59.3 | 57.3 | 47.8 | 44.8 | 545 |
| 16 | 7.55 | 25.0 | 56.2 | 54.2 | 43.7 | 40.7 | 543 |
| 20 | 8.47 | 25.0 | 54.8 | 52.8 | 41.8 | 38.8 | 542 |
| 25 | 9.51 | 24.3 | 53.3 | 51.3 | 39.8 | 36.8 | 541 |
| 31.25 | 10.67 | 23.6 | 51.9 | 49.9 | 37.9 | 34.9 | 540 |
| 62.5 | 15.38 | 21.5 | 47.7 | 45.4 | 31.9 | 28.9 | 539 |
| 100 | 19.80 | 20.1 | 44.3 | 42.3 | 27.8 | 24.8 | 538 |
| 200 | 28.98 | 18.0 | 39.8 | 37.8 | 21.8 | 18.8 | 537 |
| 250 | 32.85 | 17.3 | 38.3 | 36.3 | 19.8 | 16.8 | 536 |

Available Model

DS-1LN6USL3